| Drawings Reviewed: (titles plus dates) | Project Name: Project Number: Review By: Date: Approved By: BCDN: |
| --- | --- |

Legend: N Not required R Required C Confirm requirements or RC Review completed and item construction detail(s) indicated on documents This checklist is intended to assist architects in a review of code requirements to be considered in the preparation and review of documents to support a permit application. A simple review of the checklist is not a substitute for a thorough review of the OBC. Modify the checklist to note applicable code requirements for the project.

1. PERMIT SUBMISSION DOCUMENTS						                              OBC Code Reference(s)

|  | a | Professional design stamps & signatures | 2.3.1 |
| --- | --- | --- | --- |
|  | b | General review commitment cetter | 2.3.2 |

- 2. SIZE & OCCUPANCY REQUIREMENTS

|  | a | Major occupancy (ies) | Table 3.1.2.1, 3.1.2 |
| --- | --- | --- | --- |
|  | b | Building area | 1.1.3.2 & 3.2.2.5 |
|  | c | Number of storeys | 3.2.1 & 3.2.2.5 |
|  | d | Number of streets | 3.2.2.10.(1) to (5) |
|  | e | Building sprinklered | 3.2.5.13 |
|  | f | Classification | 3.2.2.20 to 3.2.2.83 |
|  | g | Type of construction required | 3.1.4/3.1.5 |
|  | h | Storeys below ground | 3.2.2.15.(1) to (3) |
|  | i | Fire containment in basements [600m2] | 3.2.1.5.(1) & (2) |
|  | j | Crawl space | 3.2.2.9.(1) & (2) |
|  | k | Floor assembly over basement (min. 3/4hr) | 3.2.1.4.(1) |
|  | l | Other floor assemblies (mezz. as a storey) | 3.2.1.1.(6) |
|  | m | Mezzanines/exterior passageways | 3.2.1.1/3.2.2.12 |
|  | n | Roof assembly F.R.R. (sprinkler exception) | 3.2.2.17 |

|  | o | Roof supporting an occupancy – F.S. | 3.2.2.13 |
| --- | --- | --- | --- |
|  | p | Load bearing walls and columns | 3.2.2.20 to 3.2.2.83 |
|  | q | High buildings | 3.2.6 |

- 3. SPATIAL SEPARATION

|  | a | Protection of exit facilities | 3.2.3.12 |
| --- | --- | --- | --- |
|  | b | Wall exposed to another wall | 3.2.3.13.(1) & (2) & (3) |
|  | c | Wall exposed to adjoining roof | 3.2.3.14 |
|  | d | Protection of exposed soffit | 3.2.3.15.(1) to (4) |
|  | e | Canopy projection [E,F1,F2] | 3.2.3.16 |
|  | f | Covered vehicular passageway | 3.2.3.17 |
|  | g | Buildings connected by walkways | 3.2.3.18 |
|  | h | Underground walkway | 3.2.3.19 |

- 4. PROVISIONS FOR FIRE FIGHTING

|  | a | Access above grade | 3.2.5.1.(1) to (3) |
| --- | --- | --- | --- |
|  | b | Access to basements | 3.2.5.2.(1) & (2) |
|  | c | Roof access | 3.2.5.3 |
|  | d | Access routes | 3.2.5.4 to 3.2.5.6 |
|  | e | Sprinklers: [NFPA 13/NFPA 13R/NFPA 13D] | 3.2.5.13 to 3.2.5.15 |
|  |  | : Basement>600m2 | 3.2.1.5 |
|  |  | : > 1 storey below ground | 3.2.2.15.(2) & (3) |
|  |  | : Garage below grade (except open storey) | 3.3.5.4.(7) |
|  | f | Fire alarm system required [CAN/ULC S524] | 3.2.4 |
|  | g | Standpipe system required [NFPA 14] | 3.2.9 |

- 5. REQUIREMENTS FOR MEZZANINES

|  | a | Mezzanine area: Suite or floor area: | MMezz: |
| --- | --- | --- | --- |
|  | b | Mezzanine (not a storey) | 3.2.1.1.(3) to (8) |
|  | c | Termination at vertical fire separation | 3.2.8.1 & 3.2.8.2 |
|  | d | Egress facilities / exits | 3.3.1.5 & 3.4.2.2 |

- 6. SAFETY REQUIREMENTS WITHIN FLOOR AREAS

|  | 1) |  | Means of egress |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | - Egress from roof, platform, podium |  | 3.3.1.3.(3) to (4) |
|  |  |  | - Egress roof enclosure, 2 egress if > 200m2 |  | 3.3.1.3.(5) & (6) |
|  |  |  | - Egress from service space |  | 3.3.1.3.(7) |
|  |  |  | - Each suite to have exterior exit doorway or doorway into a public corridor or exterior passageway |  | 3.3.1.3.(8) |
|  |  |  | - Access to 2 separate exits in opposite directions |  | 3.3.1.3.(9) |
|  |  |  | - Adequate egress width from rooms (Occ. Load x 6.1, 9.2, or 18.4mm) |  | 3.3.1.16 |
|  |  |  | - Egress from dwelling units |  | 3.3.4.4.(1) to (8) |
|  |  |  | - Min 2 egress doorways [F1 or occ.load > 60 or hazardous classroom > 100m2] |  | 3.3.1.5.(1):Tables 3.3.1 5A & B |
|  |  |  | - Travel distance within the room or suite when > 1 egress |  | 3.3.1.6 |
|  | 2) |  | Dead-End-Corridors |  |  |
|  |  |  | - Assembly Occupancy: second and separate egress from each room or suite not leading into a dead-end corridor |  | 3.3.1.9.(8) |
|  |  |  | ### Institutional: second and separate egress |  | 3.3.3.3.(1) |
|  |  |  | - Residential: dead-end 6m max., serves max. 4 suites, no door openings to service rooms or hazardous rooms |  | 3.3.1.9.(9) &(10) |
|  |  |  | - D,E,F-2 or F-3: dead end corridor 9m max., max. 30 occupants, self closers on doors or second and separate egress door not leading into a dead-end corridor |  | 3.3.1.9.(11) to (13) |
|  |  |  | - F-1: second and separate egress doorway |  | 3.3.1.9.(14) |
|  | 3) |  | ###### Corridors |  |  |
|  |  |  | - Fuel fired appliances prohibited in corridor access to exit |  | 3.3.1.2.(3) |
|  |  |  | - Headroom: min |  | 3.3.1.8 & 3.4.3.6 |
|  |  |  |  | - Width: min 1100 mm | 3.3.1.9 |
|  |  |  |  | : min 2400 mm serving patients | 3.3.3.3.(2) |
|  |  |  |  | : Min 1650 mm B2 or B3 occupancy | 3.3.3.3.(3) |
|  |  |  |  | - Adequate exit capacity leading to exits (Occ. Load x 6.1, 9.2, or 18.4mm) | 3.3.1.16 |
|  |  | 4) |  | Doors |  |
|  |  |  |  | - 800 mm (1 leaf) min clear opening | 3.3.1.12.(1) |
|  |  |  |  | - Operable without keys | 3.3.1.12.(2) |
|  |  |  |  | - No automatic locking device on res. suite (hotel excepted) | 3.3.4.5 |
|  |  |  |  | - Electromagnetic devices [not permitted in schools or F-1] | 3.3.1.12.(10) |
|  |  |  |  | - Panic hardware [Group A – occ load >100] | 3.3.2.6 |
|  |  |  |  | - Door swing on vertical axis from suite or room not in suite | 3.3.1.10.(1) |
|  |  |  |  | - Swing in direction of exit [F1, occ load >60, door in a corridor or exit] | 3.3.1.10.(2) & (3) |
|  |  |  |  | - Sliding doors | 3.3.1.11.(1) to (3) |
|  |  | 5) |  | Ramps, stairways, passageways | 3.3.1.13 & 3.4.6 |
|  |  | 6) |  | Guards |  |
|  |  |  |  | - Min. 1070 mm guards at roof, smoke shaft, balcony, etc. | 3.3.1.17 |
|  |  |  |  | - Max. 100 mm spacing, (max. 200 mm for F occupancies) | 3.3.1.17.(3) & (4) |
|  |  |  |  | - Non-climbable (140mm-900mm) | 3.3.1.17.(5) |
|  |  |  |  | - Guards within dwelling units | 3.3.4.7 & 9.8 |
|  |  | 7) |  | Transparent doors and panels | 3.3.1.18 |
|  |  | 8) |  | Sound transmission in dwelling units | 3.3.4.6 & 9.11.2.1 |
|  |  | 9) |  | Flammable liquids/hazardous substances | 3.3.1.2 / Fire Code |
|  |  | 10) |  | #### Volatiles prohibited in basements | 3.3.5.3.(1) to (3) |
|  | 11) |  |  | Explosion venting | 3.3.1.19 |
|  | 12) |  |  | Garage vestibules | 3.3.5.7 |
|  | 13) |  |  | Protection of floor areas with a barrier-free path of travel (see exception) | 3.3.1.7 |

- 7. REQUIREMENTS FOR EXITS

|  | a | Adequate exit capacity for each floor (Occ. Load x 6.1, 9.2 or 18.4) | 3.1.16.1 & Table 3.1.16.1 |
| --- | --- | --- | --- |
|  | b | Minimum of 2 exits | 3.4.2.1.(1) to (7) |
|  | c | One exit exception | 3.4.2.1.(2) |
|  | d | Distance between exits | 3.4.2.3.(1) & (2) |
|  | e | Location of exits | 3.4.2.5.(1) to (5) |
|  | f | Clear path of travel from exit to a safe public space | 1.1.3.2 |
|  | g | Clear width of exit, corridor, stair | 3.4.3.1.(1) to (3) |
|  | h | Required minimum exit width | 3.4.3.2 to 3.4.3.4 |
|  | i | Reduction of exit width | 3.3.1.9 & 3.4.3.5 |
|  | j | Headroom clearance | 3.4.3.6.(1) to (4) |
|  | J | Flame spread rating for exit & exit lobby | 3.1.13 & Table 3.1.13.2 |
|  | l | Fire separation of exits | 3.4.4.1 to 3.4.4.4 |
|  | m | Integrity of exits (schools – not as an “access corridor”) (no service penetrations) | 3.4.4.4.(1) to (10) |
|  | n | Exit signs and markings | 3.4.5.1.(1) to (8) |
|  | o | Sign for basement stair | 3.4.5.2 |
|  | p | Non-skid finish on stairs/ramps | 3.4.6.1.(1) & (2) |
|  | q | Minimum 3 risers | 3.4.6.2 |
|  | r | Maximum rise 3.7 m per flight (2.4m for B2) | 3.4.6.3.(1) |
|  | s | Length and width of landing | 3.4.6.3.(2) |
|  | t | Number and height of handrail | 3.4.6.4.(1) to (10) |
|  | u | Height and opening on guards | 3.4.6.5.(1) to (8) |
|  | v | Gradient and level area for ramp | 3.4.6.1 & 3.4.6.6 |
|  | w | Treads and risers | 3.4.6.7.(1) to (5) |

|  | x | Curved stair (winders not permitted) | 3.4.6.8.(1) & (2) |
| --- | --- | --- | --- |
|  | y | Horizontal exits [not permitted in schools divided by firewalls] | 3.4.6.9, 3.4.1.6 |
|  | z | Door swing | 3.3.1.10 & 3.4.6.11 |
|  | i | Sliding door in exit | 3.3.1.11 & 3.4.6.13 |
|  | ii | Panic hardware/fire exit hardware | 3.4.6.15 |
|  | iii | Emergency access (every 5 storeys) | 3.4.6.17 |

- 8. FIRE SEPARATION BETWEEN OCCUPANCIES, TENANTS, ROOMS AND SHAFTS

|  | a | Fire separation between occupancies | 3.1.3.1 & Table 3.1.3.1 |
| --- | --- | --- | --- |
|  | b | Prohibited combination of occupancies | 3.1.3.2 |
|  | c | Support of fire separation | 3.1.7.5.(1) to (3) |
|  | d | Fire wall | 3.1.10 |
|  | e | Opening in fire wall | 3.1.10.5 & 3.1.8.6 |
|  | f | Fire separation between suites | 3.3.1.1 & 3.3.4.2 |
|  | g | Fire separation of public corridor | 3.3.1.4 |
|  | h | F.S. of corridors used by public in “A” | 3.3.2.5 |
|  | i | Fire separation of janitors’ rooms (nonrated in sprinklered floor area) | 3.3.1.20 |
|  | j | Fire separation of A1 occupancy, schools: O.L. >200; hazardous rooms | 3.3.2.2 |
|  | k | Fire separation of book storage room in libraries & stages | 3.3.2.11 & 3.3.2.12 |
|  | l | Separations in care and detention occupancies | 3.3.3.2 & 3.3.3.5 |
|  | m | Separations in treatment facilities & contained use areas | 3.3.3.6 & 3.3.3.7 |
|  | n | F.S. of storage rooms in “C” occupancies | 3.3.4.3 |
|  | o | Fire separation of repair garage | 3.3.5.5 |
|  | p | Fire separation of storage garage | 3.3.5.6 |

|  | q | Fire separation of vertical transportation facilities & elevator machine room | 3.5.3 |
| --- | --- | --- | --- |
|  | r | Service room fire separation | 3.6.2.1 & 3.6.2.2 |
|  | s | Incinerator & garbage room fire separation | 3.6.2.5 & 3.6.2.6 |
|  | t | F.S. of transformer vault 3 hr…..2hr…..[sprinklers]: solid masonry or concrete | 3.5.2.8.(1) |
|  | u | Shaft fire separation | Table 3.6.3.1 |
|  | v | Fire separation at top & bottom of shaft | 3.6.3.1.(2) & (3) |
|  | w | F.S. of linen or refuse chute shaft | 3.6.3.3.(2) |
|  | x | Discharge room: linen- 1hr.; Refuse – 2hr | 3.6.3.3.(7) & (9) |
|  | y | Intake opening room ¾ hr. | 3.6.3.3.(5) |
|  | z | Horizontal service space fire separation | 3.6.4.2 |

- 9. OPENINGS IN FIRE SEPARATION

|  | a | Vertical f.s. to the u/s of floor/roof deck | 3.1.8.3 |
| --- | --- | --- | --- |
|  | b | “Membrane” exception [NOT FOR SHAFTS] | 3.6.4.2.(2) |
|  | c | Protection rating of closures | 3.1.8.4.(2) |
|  | d | Max opening in interior fire separation | 3.1.8.6.(1) & (2) |
|  | e | 20 min closure | 3.1.8.10.(1) to (3) |
|  | f | Self closers & hold-open devices | 3.1.8.11 & 3.1.8.12 |
|  | g | Door latches [glass door in unrated F.S.] | 3.1.8.13 |
|  | h | Wired glass & glass block – untested [1 hr. max. fixed wired glass, dim, structural mullions at 7.5 m2 max.] | 3.1.8.14.(2) & 5G-2 |
|  | i | Temp. rise limit [exit doors in > 3 storey, firewalls, dead end corridors] | 3.1.8.15 & 3.1.8.17 |
|  | j | Area limits for wired glass or glass block [exits, dead-end corridors and firewalls] | 3.1.8.16 & 3.1.8.17 |
|  | k | Interconnected floor spaces [F.S. at the upper floor in schools] | 3.2.8.1 to 3.2.8.11 |

- 10.  FIRE STOPPING

|  | a | Service penetrations | 3.1.9.1.(1) & (2) |
| --- | --- | --- | --- |
|  | b | Concealed spaces | 3.1.11.1 |
|  | c | Wall assemblies | 3.1.11.2.(1) & (2) |
|  | d | Between nailing & supporting elements | 3.1.11.3.(1) & (2) |
|  | e | Between vertical & horizontal spaces | 3.1.11.4.(1) |
|  | f | Roof spaces, balconies and canopies | 3.1.11.5 & 3.2.3.16 |
|  | g | Crawl spaces | 3.1.11.6 |
|  | h | Fire stop assemblies as per ULC listings | 3.1.11.7.(1) to (6) |

- 11. SERVICE SPACES

|  | a | Storage use prohibited | 3.6.1.3 |
| --- | --- | --- | --- |
|  | b | No boiler under required exits | 3.6.2.3 |
|  | c | Requirement for garbage storage | SPA |
|  | d | Door swing for boiler room | 3.6.2.7 |
|  | e | Ceiling spaces used as plenums | 3.6.4.3.(1) to (3) |
|  | f | Access to attic, service spaces, crawlspace | 3.6.4.4 to 3.6.4.6 |
|  | g | Roof anchor systems (details for buildings over 6m high) | 4.1.10.8 |

- 12. HEALTH REQUIREMENTS

|  | a | Room dimensions in dwelling units | 3.7.1.2 & 9.5 |
| --- | --- | --- | --- |
|  | b | Sleeping area in group B occupancy | 3.7.1.3.(1) & (2) |
|  | c | Sleeping area in child care facility | 3.7.1.3.(3) |
|  | d | Window in every sleeping room | 3.7.2.1 |
|  | e | Fixed windows in dwelling units | 3.7.2.2.(2) |
|  | f | Guard protection @ openable windows in dwelling units | 3.7.2.2.(3) |
|  | g | Plumbing facilities | 3.7.4 |
|  | h | Installation of X-ray machines [M.O.H./M.O.L] | 3.7.5.3 |
|  | i | Public pools [see separate checklist] | 3.11 |

- 13. EMERGENCY LIGHTING

|  | 1) | Emergency Lighting of 10 lx for | 3.2.7.3.(1) to (3) |
| --- | --- | --- | --- |
|  |  | - Exits |  |
|  |  | - Principal routes – access to exit in an open floor area |  |
|  |  | - Corridors used by the public, serving classrooms, patients’ sleeping rooms & public corridors |  |
|  |  | - Underground walkways |  |
|  |  | - Group A1 occupancy |  |
|  |  | - Group A2 & A3 if occ. Load > 60 |  |
|  |  | - Service space |  |
|  | 2) | Emergency power supply of: | 3.2.7.4.(1) |
|  |  | - 2 hour capacity for building in 3.2.6 |  |
|  |  | - 1 hour for group B not under 3.2.6 |  |
|  |  | - ½ hour for all other buildings |  |

- 14. BARRIER-FREE DESIGN

|  | a | When required | 3.8.1.1 |
| --- | --- | --- | --- |
|  | b | Accessible entrance & number required | 3.8.1.2 |
|  | c | Areas requiring B.F. path of travel | 3.8.1.3.(1) to (5) |
|  | d | Barrier-free path of travel [1060 mm min with 1600 x 1600 by-laws @30m intervals] | 3.8.2.1 |
|  | e | Access to parking areas [2100mm clear headroom] | 3.8.2.2 |
|  | f | Access to storey served by escalator | 3.8.1.4 |
|  | g | Wheelchair space in seating area | 3.8.2.1.(4) |
|  | h | Washrooms | 3.8.2.3.(1) to (3) |
|  | i | Accessibility signs | 3.8.3.1.(1) to (4) |

|  | j | Exterior walks [1100 mm min.] | 3.8.3.2.(1) to (4) |
| --- | --- | --- | --- |
|  | k | Doors and vestibules in B.F. Access | 3.8.3.3.(1) to (15) |
|  | l | Latch side clearances [door with closers] | 3.8.3.3.(11) |
|  | m | Ramps in a barrier-free access [870 mm clear; 1:2] | 3.8.3.4.(1) to (3) |
|  | n | Elevators | 3.5.4.1 & 3.8.3.5 |
|  | o | Water closet and stall [dimensions] [1.5m x 1.5m] | 3.8.3.8 to 3.8.3.11 |
|  | p | Special washrooms [dimensions 1500 mm circle] | 3.8.3.12 |
|  | q | Showers in “A” occupancy [dimensions [1500 mm wide x 900mm] | 3.8.3.13 |
|  | r | Shelves or counters for telephones & drinking fountains | 3.8.3.15 & 3.8.3.16 |